## AV-new
TEST REPORT
CUSTOMER NAME |  |  | Amtech
ADDRESS |  |  | Biratnagar, Nepal
NATURE OF TEST |  |  | AIR VELOCITY
TEST TAKEN |  |  | 12/07/2022
AHU NO. |  |  | 001
LOCATION |  |  | Tablet
DONE DATE |  |  | 2021/09/11
DUE DATE |  |  | 2021/09/11
REPORT NO. |  |  | PPE0001AV01A
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  |  | SR.NO. |  |  |  | VALIDITY
VANE TYPE ANEMOETER |  | AVM-04 |  |  |  | S12K240201 |  |  |  | 2021/09/11
OBSERVATIONS:
Room Name & ID No. | Inlet No. |  | V1 | V2 | V3 | V4 | V5 | Avg. Vel. | Inlet Size Ft2 | CFM | Room Volume (Ft3) | ACPH
Dispensing Room | F-01 |  | 40 | 50 | 70 | 50 | 40 | 50 | 4 | 200 | 1000 | 30
| F-02 |  | 80 | 70 | 90 | 70 | 80 | 78 | 4 | 312
TOTAL CFM | [9 empty] | 512
Acceptance criteria :Not less Than 20 ACPH | [6 empty] | GRADE : D
TEST CARRIED OUT BY |  |  |  |  | VERIFIED BY
PIN POINT ENGINEER |  |  |  |  | Amtech
Test Carried out by deepurana on 12/07/2022 23:57:19