## AV-new
TEST REPORT
CUSTOMER NAME |  |  | Uni Medicolabs
ADDRESS |  |  | 21-22,Pharmacity, Dehradun
NATURE OF TEST |  |  | AIR VELOCITY
TEST TAKEN ON |  |  | 19/08/2022
AHU NO. |  |  | 10
LOCATION |  |  | w
REPORT NO. |  |  | PPE0001AV01A
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  |  | SR.NO. |  |  |  | VALIDITY
Anemometer |  | AVM-08 |  |  |  | 242345 |  |  |  | 13/01/2023
OBSERVATIONS:
Room Name & ID No. | Inlet No. |  | V1 | V2 | V3 | V4 | V5 | Avg. Vel. | Inlet Size Ft2 | CFM | Room Volume (Ft3) | ACPH
ew | g |  | 90 | 80 | 80 | 90 | 80 | 84 | 4 | 336 | 1200 | 18
| g |  | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 30
TOTAL CFM | [9 empty] | 366
Acceptance criteria :Not less Than 56 ACPH | [6 empty] | GRADE : C
TEST CARRIED OUT BY |  |  |  |  | VERIFIED BY
PIN POINT ENGINEERS |  |  |  |  | Uni Medicolabs
Test Carried out by analyst on 2022-08-19 23:36:07